Ignition Gateway Database Connection Report

Datasource: site_quality_control

Prepared from screenshots of Inductive Automation Ignition Gateway database connection configuration.

Generated: 2026-07-02 06:48

# 1. Executive Summary

The screenshots show an Inductive Automation Ignition Gateway database connection configured for a PostgreSQL database. The datasource name is site_quality_control and it connects to a PostgreSQL database of the same name on server rmfplydbs01 using port 5432. The configuration appears operational and mostly default, with a modest connection pool, default transaction isolation, no connection initialization commands, and password storage embedded/encrypted by the Gateway.

The main review points are the use of the postgres database user, the Max Active connection pool limit of 8, and the Slow Query Log Threshold of 60 seconds.

| Area | Summary |
| --- | --- |
| Platform | Inductive Automation Ignition Gateway |
| Datasource name | site_quality_control |
| Database type | PostgreSQL |
| Server / host | rmfplydbs01 |
| Port | 5432 |
| Database | site_quality_control |
| Username | postgres |
| Overall assessment | Functional configuration; several production-hardening items should be reviewed. |

# 2. Extracted Configuration Details

| Field | Extracted Value |
| --- | --- |
| Datasource name | site_quality_control |
| JDBC Driver | PostgreSQL |
| SQL Translator | POSTGRES |
| Connect URL | jdbc:postgresql://rmfplydbs01:5432/site_quality_control |
| Username | postgres |
| Password mode | Embedded |
| Password visibility | Encrypted / hidden |
| Description | Blank |

# 3. JDBC Connection Breakdown

| Component | Value |
| --- | --- |
| JDBC protocol | jdbc:postgresql |
| Host / server | rmfplydbs01 |
| Port | 5432 |
| Database name | site_quality_control |

Interpretation: Ignition connects to the PostgreSQL database site_quality_control on server rmfplydbs01 using the standard PostgreSQL port 5432.

# 4. Failover, Query Logging, and Validation

| Setting | Extracted Value | Comment |
| --- | --- | --- |
| Failover Mode | Standard | If a configured failover datasource exists, connections can fail over and then return when the original datasource is restored. |
| Failover datasource | Not clearly visible / not confirmed | Check directly in Gateway configuration if high availability is required. |
| Slow Query Log Threshold | 60000 ms | Queries must exceed 60 seconds before being logged as slow. This is high for troubleshooting. |
| Validation Timeout | 10000 ms | Connection validation is allowed up to 10 seconds before timing out. |

# 5. Connection Pool Configuration

| Setting | Extracted Value | Meaning |
| --- | --- | --- |
| Initial Size | 0 | No connections are created when the pool starts. |
| Max Active | 8 | Maximum of 8 active database connections at one time. |
| Max Idle | 8 | Up to 8 idle connections can remain in the pool. |
| Min Idle | 0 | No minimum idle connections are kept ready. |
| Max Wait | 5000 ms | Requests wait up to 5 seconds for a connection before failing. |

Assessment: A Max Active value of 8 may be suitable for a light to moderate workload. It may become restrictive if the datasource is used heavily by Perspective views, scripts, reports, Transaction Groups, Tag Historian, or Named Queries.

# 6. Connection Testing Configuration

| Setting | Extracted Value | Comment |
| --- | --- | --- |
| Validation Query | SELECT 1 | Simple SQL query used to validate database connections. |
| Test on Borrow | Enabled | Connections are validated before being borrowed from the pool. |
| Test on Return | Disabled | Connections are not validated when returned to the pool. |
| Test While Idle | Disabled | Idle connections are not periodically validated by the idle evictor. |
| Eviction Rate | -1 | No idle connection evictor thread runs when non-positive. |
| Eviction Tests | 3 | Number of connections to examine per idle eviction run, if enabled. |
| Eviction Time | 1800000 ms | Connections idle for 30 minutes could be eligible for eviction if the evictor were enabled. |

# 7. Connection Initialization and Transaction Settings

| Setting | Extracted Value | Comment |
| --- | --- | --- |
| Connection Initializing Commands | Blank | No custom SQL/session commands are executed when a connection is pulled from the pool. |
| Default Transaction Isolation Level | Default | Ignition/JDBC/database default transaction isolation is used. |

# 8. SQL Compatibility and Schema Settings

| Setting | Extracted Value | Comment |
| --- | --- | --- |
| Translator | POSTGRES | Correct translator for PostgreSQL syntax compatibility. |
| Include Schema In Table Name | Unchecked | Tables may be listed without schema prefixes. Review if multiple schemas are used. |

# 9. Key Observations and Recommendations

| Priority | Recommendation | Reason |
| --- | --- | --- |
| High | Review use of postgres user | The postgres account is commonly an administrative database account. For production, use a dedicated least-privilege application user if possible. |
| Medium | Review connection pool sizing | Max Active is 8. Monitor Gateway logs and PostgreSQL activity to determine whether the pool is sufficient during peak use. |
| Medium | Lower slow-query threshold during troubleshooting | A 60-second threshold may miss poor-performing queries. Consider temporarily using 5000–10000 ms while troubleshooting. |
| Medium | Confirm failover datasource | The failover mode is Standard, but the actual failover datasource was not visible in the screenshots. |
| Low | Review schema usage | If multiple schemas exist, consider whether schema-qualified table names are needed. |
| Low | Consider session timeout controls only if needed | Connection initialization commands are blank. Add statement_timeout or lock_timeout only after confirming application query requirements. |

# 10. Useful PostgreSQL Checks

The following checks can be run by a database administrator to verify session defaults and privilege posture:

SHOW default_transaction_isolation;

SHOW statement_timeout;

SHOW lock_timeout;

SHOW idle_in_transaction_session_timeout;

SHOW timezone;

SHOW search_path;

# 11. Final Assessment

The Ignition Gateway datasource configuration is simple and likely functional. The main production-hardening opportunity is to avoid using the postgres account for normal application access. The second area to monitor is connection pool capacity, because the current limit of 8 active connections may be low if the datasource is shared by multiple Ignition functions. The 60-second slow-query threshold is fine for capturing severe issues, but it is too high for detailed performance tuning.